## Slide 1: CA Title 24 & 8 Ventilation Guidelines

## Slide 2: Ventilation Guidelines
Ventilation & Indoor Air Quality Codes:
California: Title 24, Part 6: Energy Code
  Natural ventilation: 5% of floor area is openable windows (< 20 ft away and unobstructed by walls or doors)
  Mechanical ventilation: minimum of 15 cfm/occ or 0.15 cfm/ft2 of outside air, whichever is greater.

## Slide 3: Ventilation Guidelines
Ventilation & Indoor Air Quality Codes:
California: Title 24, Part 2: Building Code
  References ASHRAE 62.1
  Mechanical ventilation: minimum requirements:
  Offices - 5 cfm/occupant (# occupants) + 0.06 cfm/ft2 (floor area ft2)
  Classrooms - 10 cfm/occupant (# occupants) + 0.12 cfm/ft2 (floor area ft2)

## Slide 4: Ventilation Guidelines
Ventilation & Indoor Air Quality Codes:
California: Title 8, Section 5142, CA Labor Code
  HVAC system shall provide at least the quantity of OA in effect the time that the building permit was issued.
  HVAC system must operate continuously during working hours.
  O&M documented in writing and made available upon employee request.