Building Operator Certification

BOC Level I

Project Workbook

Alternative Project – College Building C

Purpose: The purpose of the BOC Level 1 Project Workbook is to enable you to demonstrate your ability to apply the skills developed in the BOC classes. The five assignments in the Project Workbook require you to gather information about a facility, and provide documentation for making recommendations for improvements that would make the building operate more efficiently. If you do not have access to an appropriate commercial facility, you can use sample Building – C as the basis for completing your five required projects.

Follow the directions provided in the Project Workbook for each of the 5 projects, especially the responses identified in each Project Rubric. Instructors can advise you on completing questions where additional details may be needed to answer a question on the Rubric. If information is unavailable, indicate so on the assignment worksheets.

Background:  Building C is one of several buildings serving a community college campus in Seattle, WA. It is a concrete and brick building completed in 2007. It has two floors consisting mostly of classrooms and offices. The large space on the first floor can be divided into two separate classrooms or opened into a large single room for special events. The building operates on a twelve-month basis as follows:

- Fall/Winter/Spring (Sept-May): M-F 8am to 9pm, Sat 8am – 5pm, closed Sun

- Summer: M-F 8am to 5pm, Sat 8am – 12pm, closed Sun

- Friday evening and Saturday hours are primarily for special events

- Special events are sometimes scheduled outside of normal occupancy hours

Assignment 1 – Building Floor Plan: A set of plans are provided to assist in developing your drawings of the building systems. Washington state has maintained pace with changes to the national energy efficiency standards found in ASHRAE 90.1, so the equipment and systems in this building reflect “the state of the art” for energy efficiency in 2006. HVAC is delivered by way of one natural gas-pack AHU in a containment on the roof. Most cooling is provided to the AHU by an electric Trane DX air conditioning system. The gas heating system has an efficiency of 82% and the DX AC has an EER of 9.9.  Ductwork serves conditioned air to the workspaces through more than a dozen VAV boxes throughout the building. The VAV boxes include terminal reheat devices to help meet the thermal and air quality needs of the classrooms and offices. The student lounge near the lobby on the ground floor also has an electric radiant heater and small DX AC unit. The domestic hot water system uses natural gas.

Assignment 2 – Benchmarking: We have provided you with 1 year of monthly energy bills for calculating EUI and the cost per square foot. You will enter the building into Energy Star Portfolio Manager. www.energystar.gov

- Space Use type is Education/College facility

- Average Site EUI is 84.3kBTU/sf/yr. (national average)

- The building is 13,514 sq. ft.

- Maximum capacity of the facility is 328 students & staff. Typically, at any time during the day, average occupancy is 156 students, and 8 staff members.

- There are 17 staff desktop computers in the building. Most students use laptops as well.

- Landscaping requiring irrigation (grass, trees, shrubs, perennial groundcover plants) is 16,207 sq. ft.

Assignment 3 – Lighting Survey: Lighting equipment reflects the 2006 code requirement with most areas lit with T8 fluorescent linear fixtures, controlled by switches and occupancy sensors. Some of the areas also use daylight harvesting.  Accent lighting and parking lot lighting is mostly HID.

The assignment associated with this class asks you to research utility contacts and incentives to calculate the lighting retrofit incentive. Though this building is physically located in Washington state, for this assignment you may choose to research utility contacts and incentives relevant to your local area so that you may become more familiar with options available to you, and you may choose to use your local cost for electricity in your calculations.

Assignment 4 – HVAC Controls Review: The building systems are controlled by a DDC Building Automation System. The plan documents identify the capabilities designed into this system to provide efficient operation of the HVAC and lighting. Some BAS screenshots and pictures of the equipment are also provided. The following information will be helpful in completing the assignment:

- Occupied heating/cooling setpoints are 68/72 º F (68/70 in some offices).

- Stack/flue temps and % oxygen would require a measurement from a gauge or with diagnostic equipment to be taken at the rooftop unit. On the worksheet, you can indicate that this information is unavailable.

- Filters are changed every 3 months, and coils are cleaned annually.

- Refrigerant type is R-22

- Discharge line of compressor temperature at time of measurement was 223º F.

- On #4 of the Control Systems Review, describe the steps you would have taken to verify operation if you had access to the building.

Assignment 5 – Occupancy Schedule: The students spend approximately 50% of their school day in classes in this building and staff typically work an 8-hour day. Use this and the information provided in the “Background” section above to develop an occupancy schedule for this building. Create an occupancy profile for the building that seems realistic to you considering the building use type, and complete an analysis based on the profile you created.