## Walkthrough Plan
Walkthrough Plan Form
Student name
Building Name
City/State
Building Characteristics
Year constructed
Gross Square Feet (excluding parking)
Parking garage GSF
Will walkthrough comprise the whole building
if no, provide approximate square feet of space for walkthrough
| Space types | Y/N | GSF if present
Office
Data center/server room
Kitchen/cafeteria
Retail
Lodging
Warehouse
Healthcare
Public Assemble
Laboratory
Other
Occupancy
Additional Information (e.g. number of stories, major remodels, additions)
HVAC
Type of system(s)
Control System
Operating Hours
Interior & Exterior Loads
Type of Equipment
Control Systems
Exterior Loads
Utility Usage
Total electricity kWh consumed for the most recent 12 month period
Total natural gas consumed for moset recent 12-month period
Total Energy Use Intensity (EUI)
Is on-site solar or combined heat and power (CHP) used?
Building Walkthrough - Issues for Investigation
| Known Problems |  | See Item 15 of Scoping Interview
(eg equipment repairs needed, equipment operations problems, air leaks, noise)
Opportunities
(e.g. repair broken economizer, adjust operating schedule for office lighting to match tenant hours, relocate OSA sensor for accurate readings)
| Occupant Complaints |  | See item 10 of Scoping Interview
(e.g., hot/cold call areas, noise, rattling/humming, glare, extremely dark or bright areas, odors, dripping water)
Equipment operating schedules
| HVAC | Lighting
M-F
Sat
Sun
| Documents for Building Walkthrough | See item 16 from Scoping Interview
Division 15 and 16 Specifications
Mechanical Drawings
Control Sequence Description
Control Drawings
EMS Points List
EMS Program Print Out
Electrical Drawings
Equipment Repair History
Test & Balance Report
Manufacturer Start Up Documentation
O&M Manuals (For Controls and Major Equipment)
Additional Documents
| BOC Operational Checklists (4) |  | (see below)
Other checklists (e.g., in-house checklists) Provide examples, if available.
Other (describe):
Building Walkthrough Personnel and Tools
Meeting location, date and time
Finish location and time
Length of time per floor
What special permissions are needed for access to building spaces?
Who will participate in Walkthrough and what are their responsibilities?
Who will document the findings during the walkthrough
Tools
Flashlight with good batteries
Digital camera/Video camera
Safety gear
Portable data logger with T and Rh sensors
Toolkit for accessing filters, mixing boxes, etc.
Infrared camera
Clothes for outdoor/roof time
Tape measure
IR temperature sensor
Multimeter
Rags to clean nameplates
CO2 sensor
Hand-held radio, cell phone or walkie-talkies
Insertion thermometer
Stethoscope
Other (describe):
﻿Space What will you investigate in the space?
(See examples below. For additional examples refer to the four BOC O&M Checklists in PW Appendix.)
a. Lobby
(e.g., Look, listen, feel for airflow; Check airflow at exhaust grills and joints; Verify backdraft dampers are properly installed & operating; Exterior door leakage)
b. Mechanical and Electrical Rooms
(e.g., check HVAC temps at AHU’s – is the SAT above or consistent with building rest temp?; Hot electrical and mechanical equipment; Visible condensation; Ceiling stains)
c. Building Control System
(e.g., Review EMS programming for schedules; Verify working as programmed; Is the sequence of operation working as programmed?; Are manual mode or overrides enabled?)
﻿d. Stairwells, Elevators, and Top Level
(e.g., Air losses from stack effect; Stairwell doors or roof hatches propped open; Air sealing at top of elevator shaft; Broken windows)
e. Roof
(e.g., Roof penetrations; Water damage; Visually inspect accessible ductwork; Uninsulated attic or insulation disturbed)
| f. Tenant/Occupant Spaces |  | (pick 2 representative spaces; include spaces where occupant complaints originated)
(e.g., Blocked air diffusers; Lights and appliances left on; Look, listen, feel for airflow; Vibration; Acoustics; Odors)
g. Exterior (lighting, parking, other)
(e.g., Exterior lighting operational and off during day; Brightly lit or very dark areas; Parking garage exhaust fan operation matches occupancy)
h. Other (specify):
6. Building Walkthrough Checklists
| (There are four checklists on the following pages. Check each item that you will include in your Building Walkthrough, then use each checklist during the walkthrough to verify operation of Schedules, Outside Air, Sensors and Simultaneous Heating and Cooling.) |  |  | (There are four checklists on the following pages. Check each item that you will include in your Building Walkthrough, then use each checklist during the walkthrough to verify operation of Schedules, Outside Air, Sensors and Simultaneous Heating and Cooling.)
| In addition to the four checklists, refer to the functional test procedure you prepared for the Project Workbook Assignment #3 - Functional Test Procedure. Review the procedure and check the box below if you plan to use it during the Walkthrough. |  |  | (There are four checklists on the following pages. Check each item that you will include in your Building Walkthrough, then use each checklist during the walkthrough to verify operation of Schedules, Outside Air, Sensors and Simultaneous Heating and Cooling.)
Yes, I plan to perform the functional test during my Walkthrough.
No, I don’t plan to perform the test during the Walkthrough because (explain):
| Equipment Operation Schedules |  | Notes
Clock matches actual time (TOD and Date)
Timeclocks actually provide control
Schedules match occupancy
Optimum start enabled
Opportunity to implement optimum stop reviewed
Space temperature setpoints reflect standards of service and comfort
DHW circulation pumps scheduled
Opportunities for tenant equipment scheduling (coffee, vending, etc)
Chiller lockouts appropriate
VFDs in AUTO, fan speed/static appropriate
Boiler lockouts appropriate
Chilled water setpoints appropriate
Chilled and condenser water pump operations – appropriate
Cooling tower water setpoints appropriate
| Lighting Operation Schedules |  | Notes
Control clock matches correct time/day
Controller actually provides control
Schedules match occupancy
Night check – Lighting off
Occupancy sensors operational
Exterior lighting off during day
Atrium lights off during day
Light levels match IES recommendations
Other
| Sensor Calibration |  | Notes
OSA damper setting appropriate for temperature and time of day
Do MAT, OAT, RAT, and DAT make sense?
Boilers and chillers appropriately locked out
OSA temperature reading reasonable
OSA temperature sensor located well
Lobby pressurization issues – (building static)
Airflow through open or closed doors – (building static)
Other (specify)
| Outside Air Use |  | Notes
Minimum outside air percentage appropriate for occupancy type and # people
Lobby pressurization issues
Check elevators for airflow through open or closed doors
Check stairwell and elevator pressurization fans for damper positions (fire safety and others)
Check elevator machine room for signs of exfiltration or infiltration
Check exhaust fans for controlled dampers
Check building perimeter for signs of leakage
Economizers operating properly
OSA lockout during morning startup as appropriate
OSA lockout during afterhours as appropriate
Demand Control Ventilation opportunity
| Simultaneous Heating and Cooling |  | Notes
Chiller lockouts in place
Boiler lockouts in place
Chilled water setpoints appropriate
Chilled and condenser water pump operations appropriate
Cooling tower water setpoints appropriate
Discharge air temperature setpoints (resets)
Heating water setpoints (resets)
Insulation between unconditioned and conditioned spaces
Valve leakage through coils
Space temperature setpoints reasonably consistent in next-­to zones
VFDs operating and fan speed appropriate for anticipated loads
Review potential for reset duct static pressure
Terminal units operating cooperatively
Review potential to schedule terminal units